*Government of India*

*Ministry of Environment and Forests*

*(IA-I Division)*

*Sub:   _Summary Record of discussions of the twenty-third (23^rd )

meeting of Expert Appraisal Committee for River Valley and Hydroelectric

Projects constituted under the provisions of EIA notification 2006, held

on 16^th & 17^th February, 2009  in New Delhi._*

The list of participants is appended.

At the outset Chairman welcomed all the members of the committee.  The

committee was informed that Prof. J.K. Sharma is unable to attend the

meeting on 16.2.2009 due to unavoidable circumstances.  However, he will

attend the meeting on the 2^nd day i.e. 17.2.2009.  The Member Secretary

also informed the committee that Ministry has instructed that the

recommendation of the committee should be in clear terms i.e. either

cleared/ rejected/ further additional information. Project should not be

recommended for clearance seeking further information which is to be

examined by the Ministry.  As such all the projects which are

recommended in this fashion are to be put up to the committee.

*_Item No. 1_**     *

* *

* *

*_Confirmation of the minutes of last EAC Meeting_*

_ _

The minutes of the 22^nd meeting which was held on 22^nd January, 2009

were confirmed with the following modification:

Sl. No.2.2: Modernisation of Krishna Delta System in Andhra Pradesh:

Last line of the last para to be read as ?the clarification

should be submitted for further consideration by the EAC?.

Sl. No.2.6: Sainj Hydroelectric Project (100 MW) in Himachal Pradesh:

Last line of the last para is deleted.

Item No. 2

*_Consideration of Projects _*

*_Dated: 16.2.2009_**__*

* *

2.1       Dadupur ? Nalvi Irrigation Project in Districts ? Ambala,

Yamuna Nagar-Kurukshetra (Haryana) by Government of Haryana ?

Reconsideration for Environmental Clearance (No.J-12011/52/2008-IA.I).

This project was considered by the committee at its earlier

meeting held on 20^th November, 2008.  The reply to the clarifications

sought by the committee was considered.  It was noted that hydrology

aspects of this project is yet to be cleared by CWC.  It was also noted

that the compliance furnished does not clarify how the discharge drawn

at Hathnikund gets reduced at Dadupur pond and how the dam end (indent

MLL) is met which is col. 7, against available discharge upstream of

Dadupur (col. 6) being lower.  Do Pathrala river and _Somes_ river bring

in significant flow to Dadupur pond, which meets the shortage (demand of

Western Jamuna Canal + the new Sahabad Feeder).  How the discharge

upstream of Dadupur (in col. 6) is derived is not clear.  Further, the

required drawl of 590 cusec for the new feeder will be met is not

clarified.

The kharif irrigation requirement for paddy normally is very

high in September and early October.  The indent MLL shown in col. 7

every year (between September 1 ? October 31) is in the range of 10000

to 14000 cusec except very wet years, whereas there is considerable

shortage as in 1991, 1994, 2000, October, 2003.  How Haryana share at

Tajewala (say year 2002, in October is met when indent MLL is between

10,200 ? 12,500 cusec against 4868 ? 7509 cusec) is satisfying the

irrigation demand be explained.  The 75% dependable criteria is perhaps

not met.

The explanation given regarding flood disposal that

?villagers can also drain out flood water as per requirement by cutting

the right bank during rainy season? is not acceptable and shows

deficiency in drainage planning.  As the representatives of the project

authority were unable to explain the above issues satisfactorily, the

committee decided to depute a sub-group to visit the proposed site for

on the spot examination.  The following members were nominated:

(i)                 Dr. B.P. Das,

(ii)               Representative of CWC

(iii)             MoEF

*2.2       **Sissri HEP (222 MW) in Dibang Valley District of Arunachal

Pradesh by Soma Enterprise Ltd. for Scoping **(No. J-12011/2/2009.IA.I). *

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project.  The

committee noted that the project envisage construction of a Concrete RCC

storage dam of 204 m height on Sissiri river near Dambuk in Dibang

Valley District of Arunachal Pradesh, with dam toe power house.  The

project site is about 8 km west of Dambuk town.

About 900 hectare forest area likely to be submerged.  Major

part of the forest is unclassified forest.  Out of the 900 ha, 250 ha

has been proposed for declaring as reserved forest.  Even after

construction of the dam 25 cumec of water will always be in the river.

The name of the river is spelt as Sesseri and Sissiri in different

places. It was noted that correct spelling is Sissiri. Diesel generator

is likely to be used as source of construction power.

After carefully examining all the environmental related

issues the committee desired clarification and modification on the

following issues of the documents including proposed TOR for preparation

of EIA report.

*Form 1: *

·                    Verify from toposheet that indeed no streams will

be intercepted by the reservoir spreading over 900 ha (Item 1.22).

·                    In view of the very large inundated area by the

reservoir, a categorical ?No? to item 1.30 is unrealistic at this stage.

·                    Please inform if there is any danger to the

stability of the Sissiri River banks after the rock is extracted for the

construction work (Item 2.4).

·                    What is the reason for not considering a drinking

water component in the project *for the population in the nearby

villages* in addition to meet such demands from the project staff, in

such a large water resource development work?

*TOR*

The standardized TOR for the NE region may be adopted and any

site-specific component may be added to it for EIA and EMP. All maps

must have readable labels. If there is no Up Stream project then the

entire catchment contributing to the reservoir may be studied for

erosion class categorization and treatment of sub-watersheds under very

severe and severe classes. The DBA is to give the result in terms of

both time and magnitude of flood advancement. With respect to shifting

cultivation (/jhoom/) area, a small section may be devoted in the EIA

informing total area under /jhoom/ in the state and in the Sissiri River

basin, the currently adopted time cycle by the /jhoom/ cultivators, any

measurable or recorded impact of /jhooming/ in erosion, soil loss, land

slides and downstream sedimentation.  Impact, due to running of diesel

generator, on air quality should be studied.

*General observations*

The project involves construction of a large and high dam. The reservoir

will inundate 900 ha of forest land at FRL of which there is a part of a

proposed reserve forest also. The submergence area will be more

temporarily at MWL during passage of flood, unless the gates are

adjusted so that water level does not exceed the FRL. The river

tunneling is small.

Information on any Up Stream/Down Stream or D/S hydro-power project,

either at the execution stage or planned by the state government and CEA

may be given. It may be noted that for environmental safety and for

maintaining aesthetics, such projects are discouraged, which: (1) may

render the river flowing through tunnels for a long distance, (2)

disrupt natural river flow over long distances due to proximity of

projects and (3) do not ensure time-continuous water release in adequate

quantity from the dam towards the downstream. If any of these is

apprehended for this project by the PA, the EAC?s suggestion is to

reconsider the project design parameters to ensure environmental

sustainability, even at the cost of reducing power output. Information

on the reservoir storage volume and the time needed to fill the

reservoir from zero level to FRL and the plan of water release to the

downstream immediately below the dam during reservoir filling stage and

during the project operational stage may also be given. This may be

given in the form of a Table of comparison of monthly or fortnightly

average flow in Sesseri River at the proposed dam site without and with

the project. Most of the maps appended to the Form 1 are not readable.

* *

*PFR*

The PFR reveals that some basic hydrological and sedimentation data are

available for a limited period starting around 1992 and this will be

useful. Please clarify if ?Zero Point? means at the dam site or is a

location or a place other than the dam site.

* *

No details on the location of the project (merely mentioning catchment

area of 610 Km2 not explicit), annual, monthly rainfall series, yield,

existing / planned projects either upstream or downstream are available.

The major river to which Sissiri drains is not shown. Statement in Para

3.3.2.2 that mean annual rainfall at Dambuk is 9239.mm against 4000 mm

from isohyetals of CWC?s are anomalous.

This is a large project involving a 204 m high dam (whether storage or

run of the river not clear) with a reservoir area of 900 ha and it is

stated in 1.24 (Form 1, Activity) that ?The construction of dam would

result in formation of a reservoir and would have some impact on the

downstream flow although for a small length of the river which will be

studied during the investigations?. Such statements show the casual

approach to submitting Form 1 and ToR documents. Design energy

computations are not available for the 90% dependable year.

The authorities must submit PFR and all other data for purposeful

examination on the feasibility of the scheme.

* *

2.3       Rangit ?II Hydroelectric Project (66 MW) in West Sikkim,

Sikkim by Sikkim Hydro Power Ventures Ltd. for Environmental Clearance

(No. J-12011/6/2009-IA.I).

* *

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project.  The

committee noted that a concrete gravity dam of 40 m height has been

proposed for construction across river Rimbi Khola, a tributary of

Rathong Chhu.  Rathong Chhu then meet with Rangit river in West Sikkim

District.  The location of surface power house is near Chongjong village

on the left bank of Kalej Khola.  This is a run of the river scheme only

4 ha area is likely to be submerged.  The length of head race tunnel is

5182 m.  The project is located within Buffer Zone of Kanchanjunga

Biosphere Reserve.  The proposed project is only hydroelectric project

on Rimbi Khola.  Rangit Stage ?III Hydroelectric Project of NHPC is

under operation and in the downstream of the proposed project on Rangit

river. There is no Rangit Stage ?I project in the upstream of Rangit

Stage ?II project.

Total land requirement for the project is 64.93 ha.  Out of

which 55.87 ha is private land.  Though submergence is only 4.00 ha; the

rest of the area is required for infrastructure development and muck

disposal (9 dumping sites).  Total number of affected villages are six

and total number of affected families are mentioned in different figures

at different placed. In the presentation it is projected as 190 families

(under Baseline Data ? Socio-economic), 196 (under profile of the

projected families) and 145 household in EMP.

It was brought to the notice of the committee that in the

public hearing against question No.8, the reply was given as 10% release

of water during lean season (video recording is available), but by

mistake in the proceeding it was recorded as 15%.  Therefore, it was

corrected through a corrigendum as 10%.

It was brought to the notice of the project authorities that

sampling was not done above the dam site.  Location of degraded

catchment areas, where treatment will be undertaken have not been

identified.

The consultant clarified that sampling above the dam area

was not done and collected from the report of the ?Carrying Capacity

Studies in Teesta Basin of Sikkim? prepared by Delhi University.

The committee noted that avenue plantation has been included under

Compensatory Afforestation Plan (CAP).  This can not be part of CAP ?

this should be only Block plantation.

After critically examining all the environment related

issues the committee desired to have the following information:

(i)                 Total number of HEPs existing and planned in the

Rangit River basin, with their locations and distances from one another

to be shown in a clear map.

(ii)               Is Rangit II  the only HEP planned in River Rimbi Khola?

(iii)             The lean season flow as such is less than 2 cumec in

Rimbi Khola during January to March in the 90 per cent dependable year.

In view of this, what is the planned time-continuous minimum assured

release from the dam during these months and if such a release is

adequate to meet environmental needs for more than 5 km long river

stretch below the dam that will not experience natural flow? What may be

the flow depth and velocity in the active river section D/S of the dam

corresponding to the assured minimum release? The section on Air and

Water Environment in the EMP does not mention these details.

(iv)              The item Q 8 in Public Hearing Report indicates a 15

per cent release (of what?) and that was ?corrected? to 10 per cent

according to a letter dated 13-1-09 from State PCB to the project

developer. This will cause water to just trickle below the dam.

(v)                With respect to Q 34 in the Public Hearing Report,

why there is disagreement between the experience of the locales on land

slide and the project developer?s survey report? Land slide perhaps is a

serious issue in the region, as several people have raised this during

public hearing. The PA appears to be brushing it aside.

(vi)              The 40 m Rangit-II concrete gravity dam lies in

Seismic Zone-IV as per Seismic Zoning Map of India.  The bedding plane

in the rock (left bank of the george) dips into the george.  The bedding

plane and seismic activity may lead to landslide.

(vii)            Site specific studies need to be carried out for the

estimation of earthquake parameters.  The dam is then designed to resist

earthquake forces.

(viii)          Borrow area must be identified for mining aggregate.  It

should be so located that it should not disturb the slope stability of

the hills.

EIA

(i)                 2. /Methodology/: Number of samples taken and their

locations for all the parameters testd should have been given in a

tabular form as well as in the map vis-à-vis position of catchment area,

submergence area, dam site, down stream, power house!

(ii)               3. /Physiography/: A Contour map should also to be

provided which is essential for CAT Plan and other Management Plans!

(iii)             8. /Forest// Types/: Details should be given

specifically for submergence area, dam site, down stream, power house!

At a few places the statements under 8.2 /Ecozones/ are generalised.

For example vaguely about coniferous species/ forests, birch, juniper,

fir (common names) with no scientific names or their distribution.

(iv)              9. /Vegetation Structure/: Documentation of all groups

of plants, including Gymnosperms, Pteridophytes, Bryophytes should be

given.

(v)                10. /Faunal Elements/: Information on fauna also

appears to be for Sikkim and not specifically for the project area!

Under 10.3 /Herpetofauna/ information is for the entire State and not

for the project area!  10.4 /Butterflies/ only numbers are given and no

list is provided!

* *

EMP

(i)                 1. /Biodiversity Management Plan/: This Plan should

address RET species and rich forest types recorded in the project area

and mentioned under 9.9 of EIA Report.

(ii)               Review overall management plan with reference to cost.

(iii)             If 80% of land of any individual person is acquired,

balance land may also be acquired.

(iv)              Under water chemistry, B.O.D. has not been indicated.

(v)                Under Compensatory Afforestation Programme the

planting density should not be arbitrary i.e. 1500/ 1300 plants per ha

but it should be based on the existing plant density/ crown cover.

The above information / clarification to be submitted for further

consideration by the committee.

*2.4       **Rupsiabagar Khasiabara HEP (2x130 MW) in Pithoragarh

Distt., Uttarakhand by NTPC ? Reconsideration for EC (No.

J-12011/41/2008-IA.I.). ***

This project was considered by the committee at its earlier

meetings held on 21^st August, 2008 and 20^th November, 2008.  Replies

to the clarifications sought by the committee were considered.

With respect to clarification 4, in response to Ministry?s

letter was examined critically.  It was noted that immediate u/s project

is Sirkaribhyol ? Rupsiabagar HEP (210 MW).  If the NTPC?s project

operates with the same FRL and TWL as indicated earlier then there is no

scope for maintaining natural river flow for a reasonable stretch of

Goriganga river between Sirkaribhyol ? Rupsiabagar and Rupsiabagar ?

Khasiabara Hydroelectric Projects.

The committee noted that Sirkaribhyol ? Rupsiabagar HEP of Uttaranchal

Jal Vidyut Nigam Ltd. (UJVNL) was considered by the committee at its

meeting held in November, 2008 for TOR.  The clarification sought by the

committee yet to be replied by the UJVNL.  There is one more project in

the u/s of this project, which is not yet received in the Ministry for

clearance.

The committee noted that during lean season 2.5 cumec of

water will be released in the downstream during lean season.  It was

also noted that Central Water Commission has cleared the hydrology of

Rupsiabagar ? Khasiabara HEP.

After critically examining all the environment related

issues, the committee recommended environmental clearance to the project.

*2.5       Bodwad Parishar Sinchan Yojana, Taluka ? Bodwad, District ?

Jalgaon in Maharashtra by **TAPI Irrigation Development Corporation**

for Scoping (No. J-12011/3/2009-IA.I). *

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project.  The

committee noted that the proposed project is a joint venture of Tapi

Irrigation Development Corporation and Vidarbha Irrigation Development

Corporation.  This is a lift irrigation project.  The flood water of

Tapi and Purna rivers will be lifted during June-October through a

system consisting of jack well, pumping machinery and rising main.  The

water will be stored in two reservoirs i.e. Junone and Jamathi and

distributed mostly by gravity as well as lift.  The distribution system

will be through closed conduit i.e. pipeline.  The project is designed

to irrigate 26721 ha area of Jalgaon District and 15699 ha area of

Buldana District.

The water will be lifted from the backwater of Hatnur Dam

near Khamkhede Bridge on Purna river.  There after it will be

transported through pipeline to reservoir ?1 i.e. Junone and

subsequently to reservoir ?2 i.e. Jamathi.  The topography of the

reservoir site is such that there are hills on all sides and therefore

looks like natural bowl.  The reservoir ?1 i.e. at Junone will be

submerged 572 ha of area.  Out of which 462 ha is forest area.

Reservoir at Jamathi will be submerged 457 ha of land.  No forest land

will be submerged.  Total land requirement is 1428.64 ha.  Out of which

508 ha is forest land, 803 ha is private land and 119 ha is Government

land.  No person will be displaced for acquisition of land.  Land of 307

persons will be affected.  Though it is mentioned on page 10 under

project rationale power component however it was clarified that no power

generation is involved in this project.  Construction power will be

drawn from grid.  The proposed Terms of References (TORs) for

preparation of EIA Report was considered.  In addition of the proposed

TORs the following additional TORs were suggested:

(i)                 Three seasons Environmental Baseline Data to be given.

(ii)               Soil sampling locations in the proposed command area

for this project with 42420 ha irrigable area, may not be less than 20

each for the parts of 22220 ha under the command of Junone dam reservoir

and 20,200 ha under the Jamathi dam reservoir. The EIA report is to

contain all important soil physical and chemical parameters, chemical

property of the source water at the point of lift (near the jack well),

chemical property of the groundwater samples in the command area and

groundwater fluctuation data (pre- and post monsoon) for a number of

continuous years. The sampling locations are to be well-distributed

within the respective commands and preferably on the grid nodes of a

suitable grid lay out. The soil and water analysis results may be

discussed in terms of their potential impact on soil salinization,

waterlogging, etc.

(iii)             Elsewhere in the initial vernacular pages in the

Revised Administrative Approval document, a mention of wind energy

(/Pawan Urja/) was found. But in the Form 1 and TOR, there is no wind

energy component indicated. This may be clarified. If wind energy is to

be utilized for water pumping, the wind energy potential may be

established during the EIA and reported in the document.

(iv)              The scheme of drawal through jack well on Purna river

is not dependable without a deep point (by a barrier).  The total drawal

of 205 Mm^3 (132 + 73) for fill in two large newly created reservoirs

Junone and Jamathi will have to be drawn from a dependable storage.  The

modality of pumping of 19.14 cumec, its availability in time has to be

justified by a simulation study for 75% dependability.  It was explained

by the project authority that backwater of Hatnur Dam on Tapi (a low

diversion dam with only about 324 Mm^3 of gross storage from 59000 km^2

of Tapi Basin) has enough surplus in monsoon.

(v)                A 25 years series of yield and need of the committed

command of Hatnur dam and the 42420 ha of kharif irrigation of the lift

scheme be provided.

(vi)              No details of 40 m and 30 m deep reservoirs to be

newly created which are long earth dam projects (maximum height shown

50.03 m and 33.58 m) are available regarding foundation, competence

against seepage then catchment as well as spillway if any to be

provided.  The submergence area of 661 ha and 472 ha need to be

justified with higher affected areas of 780 and 649 ha.

(vii)            The distribution network is stated to be entirely

through underground pipes, which is being attempted for the first time

for a area of 42,400 ha in India.  The methodology be explained by a

Contour map of the entire command.

(viii)          A complete simulation of the scheme from Hatnur Tank to

Junone and Jamathi reservoirs, filling and drawal with respect to crop

water need, month wise be provided with reference to 5579 Mm^3 of

overflow water over Hatnur spillway.

(ix)              Drainage of the command area has to be detailed.

(x)                The economic viability of this Rs.1508 crores scheme

needs elaboration.

(xi)              There must be a clear map showing the sites of the two

proposed dams, the corresponding reservoir boundaries, the rivers on

which they are to be constructed, the scheme of pumping and lifting

water, the command area boundaries and the scheme of water distribution.

The two maps enclosed later in the document do not clarify these aspects.

(xii)            Assuming that the dams are to be constructed on some

perennial rivers and the river water is under some use even before the

construction of the dams and the reservoirs, information on the revised

monsoon season river flow after the water is extracted by lifting may be

given. Also, since dams will be permanent restrictions on river water

movement, the lean season flow available in the river after the

construction of the dams may also be given and its adequacy to meet the

downstream water need may be established.

(xiii)          Cross section of the reservoir including the depth of

the lake to be given.  Dam break analysis should be for all sides.

*Form 1*

(i)                 The ?Basic Information? document indicates the cost

of irrigation as Rs. 3.56 lakhs per hectare, which is too high. Please

inform the cost per unit irrigated area of some recently concluded

similar projects in Maharashtra and the all India average figure. Till a

few years back, it was well within Rs. 1.00 lakh per hectare.

(ii)               Reply to Item 1.8 is not understood. Why creation of

bund?

(iii)             Reply to Item 1.14 is frivolous.

(iv)              According to Item 2.6, huge amount of electrical

energy is needed to run the pumps. Please inform the power availability

situation in Maharashtra.

(v)                Why is the answer to Item 5.1 ?No?, in view of the

running of diesel gensets for pumping water (vide Item 2.6)?

(vi)              There is a densely populated area within or near the

project area (Item 8 of III Environmental Sensitivity). With respect to

this, is there a drinking water component in the project?

The committee approved the TOR with the above mentioned additional TORs

for preparation of EIA/ EMP report.  Revised TOR incorporating the above

points to be submitted to the Ministry.

*2.5A    Kurha Badoda Islampur Upsa Sinchan Yojana, in Districts Jalgaon

and Buldana in Maharashtra by **TAPI Irrigation Development

Corporation** for Scoping (No. J-12011/4/2009-IA.I). *

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project.  The

committee noted that this is also a similar type of project like Bodwad

Parishar Sinchan Yojana and the project authority is same.  Water will

be lifted from Purna river by constructing jack well near village

Rigaon.  The water will be pumped from jack well and will be stored in

the reservoir at Islampur Storage Dam.  The storage capacity of

reservoir is 77.690 M cum.  Two outlets are proposed to the reservoir at

either sides.  From outlet at Ch.1800 m, land from 34 villages will be

irrigated through gravity irrigation.  Total 6255 ha area will be

irrigated from this outlet.  Similarly from outlet at Ch.4860 m, land

from 22 villages will be irrigated.  Total 8331 ha will be irrigated

from this outlet.

The committee informed the project authority that as some of the members

of the committee have not received the copy of documents, decision on

the proposal will be taken only in the next meeting.

*2.6       **Cost of the **Basin study of Bichom Basin

(No.J-12011/93/2007-IA.I) by KSK Dibbin Hydrop Power Ltd. and Lohit

river Basin study in Arunachal Pradesh by M/s Athena Demwe Power Private

Ltd. (No. J-12011/34/2008.IA.I) ? Reconsideration for TOR.** *

Dr. Aman Sharma, representative of WAPCOS presented the cost

estimate of both Lohit and Bichom river basin in Arunachal Pradesh.  The

total cost for Lohit basin was projected as Rs.67.00 lakhs and for

Bichom basin as Rs.65.00 lakhs.

Considering the length and breadth of the rivers, the

committee was of the opinion that number of sampling and sampling sites

to be increased in respect of Lohit Basin study.  Cost estimate of Lohit

basin was revised and fixed at              Rs. 1 crore for carrying out

the study.

The committee approved the cost of Bichom river basin study.

Dated: 17.2.2009

* *

*Discussion with Secretary (Power) and Secretary (Environment) of

Government of Sikkim: *

As desired by the committee Secretary (Power) and Secretary

(Environment) were invited to clarify the reasons for allotting a series

of hydroelectric projects on the rivers which subsequently flows only

through tunnels and damage the environment including aquatic ecology.

Shri P. Wangchen, Secretary, Power and Dr. Anil Mainra, CCF

(representing Secretary, Environment) attended the meeting. Dr. Anil

Mainra informed the committee about the success of compensatory

afforestation and catchment area treatment. He also informed that forest

area of Sikkim has increased 2%. However, they are facing difficulty in

getting funds from CAMPA, which is delaying the implementation of

management plans.  Regarding impact of continuous tunnelling and

vanishing of original river flow and its impact on aquatic life, he

agreed that there is lacunae in implementing the Fisheries Conservation

Plan. Shri Wangchen informed the committee that Government of Sikkim has

constituted a committee to check the representations of Affected

Citizens of Teesta. This committee has recommended dropping of

hydroelectric projects in Dzongu area except two projects i.e. Pannan

Hydroelectric Project and Teesta ?IV Hydroelectric Project. He also

informed that State Government has restricted the construction of the

labour colony in Dzongu area to protect the cultural sensitivity of the

Lepchas. Due to Teesta ?IV Hydroelectric Project about 75 families in

Dzongu area will be affected due to land acquisition.  He also clarified

that there is no legal restriction for construction of developmental

projects in Dzongu. The committee requested him to give a written report

on these issues to all the members, which he agreed.

*2.7       Teesta Stage -IV Hydroelectric Project (520 MW) in Sikkim by

NHPC Ltd. for Scoping **(No. J-12011/67/2008-IA.I.).** *

This project was considered by the committee at its earlier

meeting held on 21^st November, 2008. The PA was requested to attend to

three further requirements of the EAC, one of them being the replies to

the various representations. On the contentious issues of encroaching

upon the Lepcha Reserve and dam height, the perceptions and views of the

PA and the representing organizations are differing all the time. On

another of very important issue of tunneling of Teesta over long

stretches due to three cascade projects, the committee noted that the

project authority cites CEA?s planning and recommendation on power

development potential of the river.  The committee was of the opinion

that the projects, which are under operation or under advanced stages of

construction, cannot be asked to change their design now to allow longer

stretches of natural flow or reduced tunneling of Teesta. But the future

projects, as is the case with Teesta IV, have the option to redesign

some of the components that may allow lesser length of river tunneling

or lesser disturbance to natural river flow, even at the cost of some

amount of power generation. In this way, the cause of environment will

be served better.

The issues raised in the representations of different

organisations were clarified by the NHPC.  It was noted that Dr. M.K.

Pandit of CISMHE, Delhi University who was Principal Investigator in the

Carrying Capacity Study of Teesta Basin in Sikkim has clarified vide his

letter dated 13^th February, 2009 that the 80 m height for the dams

below Chungthang is with reference to river bed level.

Regarding allowing the last remaining free flowing stretch

of Teesta river in Sikkim to continue to flow free.  NHPC stated that

out of six projects, NHPC has been allotted two projects namely Teesta

Stage ?V project (510 MW) & Teesta Stage ?IV project (520 MW).  Due to

decision taken by MoEF two projects namely Teesta ?I & II shall not be

considered for Environmental Clearance.  5.2 cumecs of water shall be

released from Teesta ?IV dam perennially, as environmental flow.  In

addition to this, around 9 perennial streams between Dam and Powerhouse

will contribute around 6.55 cumecs to Teesta river even during lean

season.

As per the CWC layout, the planned FRL of Teesta ?IV H.E.

Project was EL 768 m with its dam near Namprikdang Mela Ground, which

was further shifted d/s to EL 755 m.  Subsequently, TRT of Teesta ?III

was shifted d/s from EL 768 m to EL 755 m which was not objected to

either by Dzongu people or by SANDRP. It was decided to obtain necessary

clarification from Teesta- III authorities about shifting of TRT of

Teesta-III for EL 768 to EL 755 and also obtain whether they had taken

permission from the concerned authority and if such permission was

granted, under what circumstances such permission was given.

Regarding impact on Dzongu area NHPC has clarified that the

original location of the dam, proposed by CWC, was at Sanklang which

fell upon the Namprikdang mela ground.  On request of the people of

Dzongu and Government of Sikkim, NHPC decided to shift the location of

the dam from the said mela ground to about 3.5 km downstream near

confluence of Runchu with Teesta.  Further, the FRL has been lowered by

about 13 m, from EL 768 m to EL 755 m to avoid submergence of mela

ground. Further, respecting cultural sensitivity of Lepcha community,

layout of the project has been modified/ evolved in such a manner that

it will cause least disturbance. In Teesta ? project, where two nos.

Diversion Tunnels and right abutment of Dam lie in Dzongu area,

respecting the sentiments of the people, neither NHPC nor its

contractors constructed any temporary/ permanent offices, colony or

stores in the Dzongu area. On request of Dzongu people, a big Gumpha has

been constructed in Lum village. Also, infrastructural works, like

construction of CC footpath leading to Lum village, providing GI pipe

ralling along the footpath from Dam site, cosntruction of police check

post have been done in Dzongu area, to provide them better connectivity

with other parts of Sikkim.  Lot of works under Teesta ?V HEP Catchment

Area Treatment scheme, were done in Dzongu area with locals?

participation, to improve the environment.

It was brought to the notice of the committee that as per

EIA Notification, 2006 decision on finalisation of TOR needs to be taken

within 60 days.  The committee was of the opinion, in view of a number

of representations received from Affected Citizens of Teesta, SANDRP and

Kalpvriksh and after critically examining all the environmental related

issues, the committee decided to visit the site before taking a decision

on the proposal.

It was also decided that MOEF may be requested to allow the

committee to hold its meeting for the month of April 2009, in Sikkim

along with the site visits to hydro-electric projects on Tessta river,

so that members of the committee may examine the issues raised by

different Civil Societies regarding vanishing of Teesta river in tunnels

and impact on protected area for Lepcha community i.e.on Dzongu.

2.8       Upper Bhadra Lift Irrigation Project Stage-I in Chikmagalur

District, Karnataka ? TOR (Adequacy of EIA) (No. J-12011/7/2009-IA.I).

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project.  The

committee noted that the project authority has already prepared the EIA/

EMP report without scoping. As such committee decided to examine the

adequacy of TOR which was considered for preparation of EIA report.

The committee noted that the project involve lifting of

water from Tunga river to Bhadra reservoir in two stages. The dam

already constructed for Bhadra reservoir. There after construction of

canal from Bhadra reservoir to delivery chamber including three lifts

and a tunnel of 6.90 km length and canal network to provide irrigation

facility to 1,07,265 ha of land in Chikmagalur and Chitradurga Districts

including filling of 37 tanks situatted within the command area.  Total

land requirement is 5245.37 ha.  Out of which 230 ha is forest land.

The length of main canal is 180.30 km. Bhadra Wildlife Sanctuary is in

the vicinity of the proposed project. The nearest point of the main

canal is 3.5 km from Wildlife Sanctuary.

The committee noted three seasons data for baseline

environmental study has been considered.  These are winter season

(Dember, 2007 to February, 2008), pre-monsoon season (March, 2008 to

May, 2008) and monsoon season (June, 2008 to September, 2008).  The

study area included 1 km on either side of the proposed alignment of the

scheme.  Area within 10 km radius from the existing Bhadra dam and

entire command area (irrigable command area) i.e. 1,07,265 ha in

Chikmagalur and Chitradurga Districts.

After critically examining all the environment related

issues the committee desired that the following issues needs to be

incorporated in the EIA report:

* *

*Form 1*

* *

(i)                 The cost of irrigation comes out to be approximately

Rs. 3.2 lakhs per hectare. Is it not too high? Till some years back, it

used to be less than Rs. 1.00 lakhs per hectare for a major irrigation

project.

(ii)               Please reconsider the reply ?No? to Item 1.15 in view

of presence of construction workers, long term housing for O & M staff, etc.

(iii)             Is the Almati dam at the downstream of the proposed

project? If so, please clarify if permanent withdrawal of 21.5 TMC of

water every year from the rivers Tunga and Bhadra may reduce the inflow

to the reservoir of the Almaty dam.

(iv)              What is the status of clearance of area under wild

life sanctuary, state forest and reserve forest?

* *

*TOR*

* *

Base line study of soil texture in the command area is missing.

*Summary Report*

* *

(i)                 The PA may please explain the methodology adopted to

arrive at the Total Impact Score (TIS) and its interpretation.

(ii)               Water quality has been reported with respect to

drinking water quality norms of BIS. Please note that water pH of 8.5

(in fact above 8.0) may prove hazardous for cultivated soils when: (a)

water application is to continue for long years, as in an irrigation

command area; (b) soils are heavy; (c) internal soil drainage is poor

(d) summers are extreme. Soil and water quality may further aggravate,

as irrigation will be in the monsoon season only and there will be no

water to dilute and wash away the salts accumulating over the long dry

season.

(iii)             Sampling sites for soil and water are stated to be 38.

Please give the numbers separately for the 2276 ha of irrigated area in

Chikmagalur district and for the 104989 ha of irrigated area in

Chitradurga district.

(iv)              Please clarify if the temperature information given on

Page 14 are for Chikmagalur district, Chitradurga district of average of

both.

(v)                The information on Socio-economic Environment does

not reveal the economic status of the population under various

categories and in different regions.

(vi)              Waterlogging and salinity problems are proposed to be

tackled by adopting bio-drainage measures. Has the PA found any evidence

in India where bio-drainage has been practiced at a command area scale

and has been successful in saving agricultural land from waterlogging

and salinity? Very little is known on the effectiveness of bio-drainage

on agricultural lands as a remedy for salinity and waterlogging. Till

date, there is no substitute for conventional drainage methods in the

command area scale to address the salinity and waterlogging issues. This

is a part of the standard OFD works and it should not be ignored or

diluted in such a large scale flow irrigation project.

(vii)            Table 17.2 misses three important environmental

parameters relevant to the soils of an irrigation command area. These

are progressive changes in soil quality from surface down to the active

crop root zone (mainly pH, EC and Na^+ ), groundwater quality and

groundwater table. These are to be included in the monitoring programme.

*EIA-EMP Report*

The EIA-EMP document has 519 numbered pages, plus about one-third of

this as unnumbered pages plus some more unnumbered pages at the

beginning plus some maps. All pages are printed on one side. It weighs 5

kg. This huge document was provided about a week before the scheduled

date of meeting. It is extremely difficult to even handle this treatise,

what to speak of reading, comprehending and giving relevant observations

on the material contained in the document. This observation may please

be taken seriously by the PA while preparing reports for the subsequent

projects.

*Chapter 1* does not say if soil texture, water infiltration rate,

saturated hydraulic conductivity and presence of hard pan below the soil

surface were also determined at the selected sampling locations. All of

these parameters individually and in combination determine

sustainability of irrigation. How many sampling points were involved for

some of these values given in the questionnaire? Was the command area

classified in terms of  land irrigability?

*Chapter 3* mentions that drip and sprinkler irrigation would be

mandatory 3 years after start of irrigation (Page 35). Is there any

legislation for this? What may the government?s support to the farmers

to switch over from flow irrigation to drip and sprinkler methods? Are

there adequate infrastructures of the concerned industry/dealer/

supplier/after sales service, etc., for motivating the farmers to adopt

this system of irrigation? Which crops among those listed under the

?proposed plan? in the questionnaire are proposed to be brought under

this mandatory irrigation plan?

The lining features, as given in the questionnaire should have also been

mentioned in Page 38. Will the irrigation water be measured at any level

of distribution? Will there be some sort of rostering for irrigation

water distribution. Are there already existing or planned water users?

associations for better management of irrigation water?

Multiplicity of benefit:cost ratios (Pages 58, 60, 62 and 64) are

confusing. It would suffice to give the value that has been adopted and

the methodology of calculating that.

Much of Chapter 3 is not relevant as EIA study and may be more relevant

in a DPR.

*In Chapter 5*, Pages 78 to 87 do not give any base line information.

*In Chapter 6*, most of the materials from Page 88 to 92 and 94 to 104

are redundant. In the legend of the map of Fig. 6.1 on Page 93, there

are certain numbers. They do not seem to be the percentage area under

different doil textural classes. What are they?

The break up of the soil sampling stations (Table 6.5) does not reveal

the station identity with respect to the command areas in the two

districts. Sampling locations are best shown in a map, rather than by

descriptions of the locations.

All pH values in Table 6.6 are below 8.0 except one (8.1 in S33). The EC

values are also low (if they have been expressed in m mhos cm ^-1 ).

Hence, chemically, the soils are good for irrigation.

Though Table 6.6 is for physico-chemical properties of soil, physical

properties such as soil mineral composition, water holding capacity,

porosity, bulk density, etc., are not found there.

As, there is no catchment area to be considered for this lift irrigation

project, why four pages (Pages 118 to 121) on soil erosion and such

remedial measures that are not practiced on cultivated lands? If soil

erosion in the proposed irrigated command area is considered a hazard,

then the methods to control that are entirely different. The encircled

area in the map of Fig. 6.3 (Page 121) shows negligible to moderate

erosion hazard in the command area. Whole of Karnataka is not relevant

for the EIA study of one project in Karnataka.

*In Chapter 7* again, lot many pages (Page 122 to 142; 165 to 167)

discuss generalities, which are known and are not specific to the EIA of

a specific project.

The water quality sampling locations W30 and W34 differ very little in

their latitude and longitude. At both the places, bore well water

samples were analyzed. In view of this, the great difference in the pH

values (8.6 and 6.8, respectively) in Table 7.6, Page 146 in the same

(winter) season is surprising. The probable cause of this variation is

not indicated. The water quality, however, is quite good for irrigation

by both surface and groundwater. What remains unclear though is the

occurrence of medium salinity in 82 samples both during the pre-monsoon

season and the monsoon season (Tables 7.14 and 7.15 on Pages 158 and

159, respectively). Why there is no dilution effect on salinity during

the monsoon season?

What is the relevance of the section on soil erosion from Bhadra dam

catchment?

* *

*In Chapter 8*, Air Environment has been presented in great details. It

is not so much relevant for an irrigation project and a few pages would

have sufficed to highlight the impact on air environment during the

construction phase.

*In Chapter 9*, large quantity of irrelevant information has been packed

(eg., hourly wind pattern for 2 years, which is repeated later under

different seasons, Figs. 9.1 to 9.12, Figs. 9.13 to 9.24 and the large

sub-section o noise). The report does not reveal how the impact of these

parameters become important for consideration in an irrigation project

and warrant adoption of management measures to mitigate them. This may

be clarified during the presentation.

*In Chapter 10*, none of the information from Page 222 to Page 231 could

be linked to irrigation activity (how irrigation may cause harmful

changes in the base line noise condition).

*The Chapter 11*: Socio-economic Environment gives vast amount of

information, including information that are irrelevant for this Chapter

(eg., Details of Vani Vilasa Sagar Dam, rainfall pattern, 10-year

rainfall data in Figure and also in Table, agro-climatic zones of

Karnataka, Climatic regions of India, Geological map of Karnataka, and

so on and so forth. But it gives no information on the economic status

of the population in the project region vis-à-vis in Karnataka state or

other regions of the state to highlight the importance of bringing

irrigation to the project area.

*Chapter 13* presents the GIS and RS application in the EIA study. The

maps, however, have legend, which are too small in font size for

reading. Besides, the reason of giving so many pages for micro-watershed

details and how these have been used for planning of some activities

related to irrigated agriculture are not clear.

*Chapter 14* discusses Environmental Impact Assessment. Many impacts

have been perceived as a consequence of project construction and

operation. Most of these are stated to be of low magnitude, having no

substantial adverse impact on the environment. When the perceived

impacts are substantial, appropriate measures would be taken. But it is

observed that the measures to mitigate the adverse effects are mentioned

in imperative term such as: ?muck disposal yard needs to be

strengthened? (Page 420); ?bank restoration may be required ? (Page

420); ?corrective measures need to be worked out? (Page 420); ?efforts

may be made for proper citing of these facilities? (Page 421);

?compensation needs to be worked out? (Page 423) and so on and so forth.

Since later in the EMP organizations/agencies have been identified for

different management activities, such presentations in this Chapter in

imperative terms are redundant. EIA should be restricted to assessing

impacts and their significance and severity.

Surprisingly there is no mention of the possible impacts on the soil and

water environment of the proposed command area, hitherto under rainfed

agriculture, after introduction of irrigation. Post-irrigation

development of soil salinity, alkali condition, surface water

congestion, water table rise, very low irrigation efficiency,

inequitable distribution of irrigation water, the tail enders? problems,

etc., are so common in the irrigated commands in India that ignoring

these issues in EIA and EMP will be a great error. It is necessary to

identify them and suggest suitable measures identifying the agency to be

responsible for adopting the measures.

While highlighting the ?overall development and upliftment of the

socio-economic status of the villages, especially in the command area?

(Page 429), the statement would be more meaningful if it was supported

by information on agricultural productivity, production and income from

agriculture at present and those that may be anticipated after

introducing irrigation in the proposed command area.

*Chapter 15* discusses Environment Management Plan. The impacts, their

management and identification of the managing entity are very well

presented during the construction phase. The 3^rd bullet on Page 447

assures that no earthwork would be done during the rainy season to avoid

water contamination due to soil wash out. As such, during the monsoon

season it is a practice not to undertake earthwork because it is not

possible to do so. It will be more difficult in the heavy soil regions

in the command area. Hence, this is a superfluous statement. It would be

more important to take care of the loose earth generated in the dry

season prior to the onset of monsoon. Please enlighten how this is

proposed to be done with respect to the loose earth generated for canal

construction, land clearance and other constructional activities.

The budget provision for medical facilities (Table 15.3, Page 452) is

far too inadequate. Which manufacturer in India will sell an ambulance

at Rs. 1.75 lakhs only and what sort of equipment, lab facilities,

furniture etc., can be purchased in Rs. 1.75 lakhs? Please provide a

realistic budget for these and if possible, please identify which lab

equipments will be procured.

Unnecessary details have been provided in sub-section 15.10.2 for

activities that are to remain restricted over a very small area in

comparison to the proposed irrigation command area. For the later,

nothing is mentioned on the effort by the PA or some concerned

department of the state to maintain soil and water health after

introduction of irrigation water, which would be alien to the hitherto

rainfed land.

*Chapter 16* discusses Command Area Development Plan. Does command area

development comprise bio-drainage and conjunctive use of surface and

groundwater only? What about land development, field channels, field

drains, proper cropping pattern, water rostering, water measurement,

improvement of field application efficiency of irrigation water,

adoption of water saving irrigation methods, etc.? Will they come up

automatically at farmers? cost? Besides, what is written on bio-drainage

is purely a conjecture and my sincere suggestion to the PA is to give

this a very low priority and only on experimental basis over some small

waterlogged and saline patches of the command and not project it as a

solution of waterlogging and salinity problems before such corroborative

data are obtained from the experimental work. The EIA has failed to

recognize command area land and water as the entities, which are likely

to experience adverse impacts the most in an irrigation project and

naturally, the EMP has not addressed this issue at all. On conjunctive

water use, it was noticed that a Table giving the discharge potential of

different types of groundwater structures. It is also important to

highlight the energy availability to the farmers for water lifting.

*Chapter 17* discusses the Environmental Monitoring Programme.

Monitoring of soil and water health in the command area is conspicuously

absent in this Chapter. Please include at least the following: (a) Soil

chemical parameters, mainly, salinity, pH, nutrient status and

concentration of major pesticides and insecticides, as applied by the

farmers; (b) Pre- and post monsoon groundwater table depth and (c)

surface and groundwater quality. Besides these three, it will be very

useful if the monitoring programme includes information on the progress

in various command area development activities and actual irrigation

efficiency (mainly, the field water application efficiency) to ascertain

how the irrigation system is working.

*Chapter 18* is on Seismicity and Disaster Management. It would be more

appropriate for an irrigation project to discuss the effect of continued

drought situation in the catchment that may reduce water availability,

water lifting and water distribution, causing distress to the farmers

who will get used to irrigation facility.

* *

*The subsequent pages* contain huge volume of information on ?Monthly

Returns of Hydro-meteorological Stations. All these are occupying about

one-fourth of the 5 kg report. These are redundant in an EIA/EMP

document. A brief summary could have been given in a properly developed

format and in a few pages to reduce the burden.

The reason for preparing the EIA/EMP report without obtaining prior

environmental clearance needs to be clarified.

Comment from Chief Wildlife Warden of State Government to be submitted

regarding impact of this project on Bhadra Wildlife Sanctuary.

The EIA to be revised according to the above observations of the

committee and resubmitted for further consideration by the committee.

2.9       Arakot Tiuni HEP (81 MW) in Dehradun District, Uttarakhand by

Irrigation Department, Government of Uttarakhand for Scoping

(No.J-12011/1/2009-IA.I).

The representatives of the project authority gave a detailed

presentation on the salient features of the proposed project. The

committee informed the project authority that some members of the EAC

have not received the documents. Hence, the committee will only listen

to the presentation.

The committee noted that site clearance under EIA

Notification 1994 was accorded to this project on 7.3.2005 by the

Ministry for generation of 72 MW. However, as they could not complete

the EIA report preparation, they have submitted the proposal again as

the new EIA Notification 2006 has supersided the 1994 Notification. It

was noted that construction of a 62 m long barrage across river Pabbar

near Arakot village in Uttarkashi district with river bed level 1199 m

above MSL has been proposed for generation of 81 MW. River Pabbar is a

tributary of river Tons which is a tributary to river Yamuna.The

proposed project area forms a part of Pabbar Valley which originates

from the hills of Himachal Pradesh. On the up stream of the proposed

project; in Himachal Pradesh construction of Swara-Kuddu HEP is in

progress, which was granted EC in May 2007.

Total land requirement is 38 hectare. Out of which 31

hectare is forest area and irrigated agriculturtal land is 7 hectare.

The water will be diverted from barrage to the power house through a

11.10 km long tunnel.

The committee noted that the PFR prepared in 2003, when the

proposal was submitted for 72 MW. However the present proposal is for 81

MW. Necessary changes has not been done due to change of capacity of the

project.

After the presentation, the committee pointed out the

followings:-

*Form 1*

A very long stretch of the River Pabar will get tunneled (11 km from

Barrage to the Power House: Item 1.9). What may be the possibility of

reducing the length of river tunneling, either by selecting an alternate

site or by reducing power generation?

The answer ?No? to many issues is incompatible with the observations

given in the last column (1.22, 1.23, 1.24, 3.1, 5.3, 5.5, 8.1, 8.3, etc.).

*TOR*

It is suggested that the TOR may contain items that would permit

assessment of the project by looking at scenarios of reduced river

tunneling length and consequent reduced power generation. In any case,

vanishing of the original river course for 11 km at a stretch for a

single project is unfriendly to environment and aesthetics. If the

secondary data sources contain observed sedimentation rate at or near

the proposed barrage site then it is OK, otherwise, during the 1-year

EIA, primary data on sedimentation may be collected. There is no item in

the TOR for CAT. Please note that CAT plan may be developed after

identifying sub-watersheds under various erosion categories following

the SYI method and this is to be done for the entire catchment if there

is no upstream project or for the free draining catchment otherwise.

The TOR may also focus on scientifically establishing the ecological

water need and the corresponding time-continuous minimum release

immediately downstream to the barrage during the lean season.

*PFR*

The adequacy of the lean season release of 1 cumec (10% of the average

non-monsoon flow; Page 3) to meet environmental needs is to be

established with water and flow requirements for different biological

entities immediately downstream to the barrage.

The Recommendation 2 on Page 28 is not clear. Has the proposed 30-year

observation on annual peak flood started? Is the indicated gauging site

the same as the barrage site of the project? Is the present study based

on the annual maximum daily discharge at the proposed barrage site? What

is the length of record of record of annual maximum daily discharge?

It is seen from the discharge data of Table A (Page 34 onwards) that

even during the lean season (December to March), the flow reduces to

less than 10 cumecs only in occasional years. In view of this, minimum

release of just 1 cumecs from the barrage into Pabar River may be highly

inadequate.

As all the members of the committee have not received the

documents, the project authority  was requested to ensure that all the

members received the copy and attend the next meeting.

*2.10    Polavaram Multipurpose Project in Andhra Pradesh by Government

of Andhra Pradesh ? Reconsideration for EC (No. J-12011/74/2005-IA.I).* **

This project was accorded environmental clearance during

October, 2005.  On a petition filed by Shri Laxman Munda in the High

Court of Orissa the Hon?ble High Court in its order dated 22.3.2006

directed that ?it is open to the State of Andhra Pradesh to proceed with

the construction of Indira Sagar (Polavaram) Multipurpose Project after

complying with the requirements of all laws applicable in this regard,

in such manner that no land/ village/ area situated within the territory

of the State of Orissa is submerged?.  Following the above order of

Hon?ble High Court of Orissa MoEF communicated to the Government of

Andhra Pradesh vide letter dated 25^th April, 2006 that the direction of

Hon?ble High Court of Orissa also may be treated as an addendum to the

above environment clearance letter dated 25^th October, 2005.  Academy

for Mountain Environics filed a petition in the National Environment

Appellate Authority (NEAA) against environment clearance to this

project.  This project involve submergence in Chhattisgarh and Orissa

also.  NEAA quashed the environmental clearance as public hearing was

not conducted in these two States.  Andhra Pradesh Government challenged

the order of NEAA in the Andhra Pradesh High Court.  Andhra Pradesh High

Court granted stay on the order of NEAA and allowed the construction

work on the project.

The proposal was referred by Central Water Commission to

this Ministry for comments for consideration by the Technical Advisory

Committee (TAC) on irrigation, flood control and multipurpose projects.

The TAC note circulated for this project, stated on page 15 that the

State Government of Andhra Pradesh has reassured vide letter

No.42137/Maj.Irrgn.I(1)/2008 dated 10^th January, 2009 that by

undertaking adequate measures through bunds/ embankments, drainage

sluices and pumping arrangements, no land will be submerged in Orissa

and Chhattisgarh and there will be no displacement of any population.

As construction of bund on the river was not considered by

the then Expert Appraisal Committee, neither details were given in the

EIA/ EMP report, the Ministry wanted to examine the impacts on

surroundings for construction of the proposed bunds etc.  As such the

details of construction of bund was submitted to the Ministry for

appraisal.

Shri S. Joshi, Secretary (I&CAD) gave a detailed presentation on the

proposal.  He stated that the scope of the project has not been changed

because the height of the dam, FRL, benefits contemplated and all other

project parameters remain same and unaltered.  The project works are in

progress and an expenditure of Rs.2239 crores has already been incurred

so far on various components.  The project authority has proposed

embankments on Sabri river and Sileru river.  Length of protective

embankments is 30.20 km in Orissa and 29.12 km in Chhattisgarh.  The

embankments are broadly divided into three reaches depending upon the

height of embankment.  Under reach ?I (river Sileru), 0-10.472 km will

be covered with varying height upto 10 m, reach ?II (river Sileru and

Sabri) the length will be 10.472-16.43 km and the height of embankment

will be between 10 m to 15 m, for reach ?III (river Sabri) the length

will be from 16.43-30 km and the height of embankment will be up to 10

m.  Total quantity of muck will be generated due to excavation of

cut-off trenches is likely to be to the tune of 5.4 lakh cum.  Out of

which 2.623 lakh cum will be in Orissa side and 2.77 lakh cum in

Chhattisgarh side.  This muck will have useful soil for embankments to

an extent of 3.48 lakh cum.  The muck generation due to topsoil removal

is estimated to be 4.64 lakh cum in Orissa and 5.36 lakh cum in

Chhattisgarh.

Shri Joshi further stated that expenditure for construction

of embankment would be costing the Government an estimated expenditure

of about Rs. 600 . 00 crores, whereas the best of R & R package for few

affected village population would have been only about Rs. 60.00 crores.

This huge infractus  expenditure has been planned due to opposition of

both the States of Orissa & Chattisgarh; which would have immensely

benefited the affected villages and people of Orissa & Chattisgarh.

* *

Dr. B.P. Das has made the following observations on the proposal

submitted by the Govt. of Andhra Pradesh

(i)                 The reservoir to be created is likely to back up

along the two major tributaries, Saberi and Sileru submerging the

overbank low lands in the States of Chhattisgarh, Orissa and also in

Andhra Pradesh.

(ii)               No reservoir in India has embankments in its

periphery to restrict the spread, which in turn creates stagnation of

water during monsoon and also deprives the reservoir of its natural yield.

(iii)             The area of submersion to be protected by embankments

be indicated with their elevation from the deepest point to FRL of

Polavaram (+150 Ft.)

(iv)              Although pumping is proposed, it can not be considered

full proof because of the cyclonic storms.  Chhattisgarh, Orissa and

Andhra Pradesh experience (in May, 1990 A.P. got 1000 mm in Kakinada in

3 days, Orissa in September, 1980 got 500 mm in 2 days) cannot be pumped

out even 7?8 days.

(v)                The most important issue is large reservoirs with

high spillway capacity have been constructed on Kolab (Saberi), Balimela

and Lower Sileru on Sileru.  These reservoirs will be required to spill

design overflow in September-October during cyclones that will impinge

on FRL of Polavaram.  This will create much larger backwater rise, not

anticipated now.

(vi)              Public hearing is mandatory in upper States for an

inter-State project.  No information is available in this regard.

(vii)            A lower FRL at Polavaram vis-à-vis the demerits of

submersion in Chhattisgarh/ Orissa need examination.

In this connection the committee noted that CWC which is the highest

competent authority of the Govt. of India has already approved the

proposal of the Govt. of Andhra Pradesh for construction of embankments

after taking the various relevant technical factors into consideration

and after the approval given by the CWC, the Govt. of Andhra Pradesh

approached the Ministry of Environment and Forests for environmental

clearance for construction of Embankments.

The committee also noted that the present proposal is for the

construction of protective embankments along the Rivers Sabari and

Sileru with a view to avoiding any land submergence in the states of

Orissa and Chhattisgarh, as directed by the Hon?ble High Court of

Orissa. It also noted the project was already given environmental

clearance for the other components during 2005 and construction of

embankments now proposed does not change the scope of the project which

was cleared earlier.

It was also noted that the concerned authorities of

Government of Chattisgarh and Orissa have not been informed about

construction of embankment on Sabri and Sileru River on the banks

located in these two States. It was not clear to the committee, how the

construction of embankment is possible without co-operation from the

concerned authorities of Governments of Chattisgarh & Orissa,.However

the Committee noted the submission made by the Secretary (I&CAD) that

earlier efforts made by the Govt. of Andhra Pradesh with the concerned

authorities in Orissa and Chattisgarh to conduct public hearings in the

respective states did not yield any responses in the past.

After critically examining all the environment related

issues, the committee agreed with the technical content and contentions

of proposal to construct embankments in Orissa and Chhattisgarh over

small sections of tributaries (Sabri and Sileru river and their

tributaries.).  This is also the requirement of the decisions taken by

various Courts of Law and to avoid submergence in Orissa and

Chhattisgarh by other competent authorities.  The Expert Appraisal

Committee while agreeing to the proposal, however, finds the statutory

requirement of public hearing as mentioned in the EIA Notification, 2006

was not conducted in Chattisgarh & Orissa. The EAC therefore directed

the project proponent to initiate suitable action requesting the

appropriate authorities in Orissa & Chattisgarh for conducting public

hearings in the respective states of Chattisgarh & Orissa in respect of

embankment proposal and report back to the committee.

*_Item No.3_*

*            Any other item with permission of the Chair.*

Krishna Marathwada Irrigation Project at Osmanabad in

Maharashtra  was considered by the committee in its meeting held during

October 2008 and committee approved the proposed T O R subject to

submission of certain clarification, which need not be put up to the EAC

again. The project authority submitted the clarifications in January

2009. The Ministry wanted that these clarifications should be approved

by the EAC. This was considered by the committee and accepted the

clarifications submitted by the project authority. The Ministry may now

process the proposal for approval of T O Rs.

It was decided that next meeting will be held on 19^th and 20^th March,

2009.

The meeting was ended with thanks to the chair.

*The minutes of 23^rd EAC meeting are confirmed*.

*

(P. Abraham)*

*

Chairman*

******